CA-D-317A Filter, Desiccant, and Separator Change Records

Controlled maintenance closeout extracts for reconciliation

Document reference: FCR-CA317A-2026-06 | Issue date: 2026-06-24 | Package: CA-D-317A

# 1. Record scope and authority

This record consolidates completed filter, desiccant, purge-valve, gasket, and oil-separator work. Completed installation checks and field label verification control installed part identification. Store descriptions and vendor quote status are retained only as supporting or conflicting evidence.

# 2. Current filter change closeout

| Record | Date | Component | Installed part | Batch | Material/config | Closeout | Verification |
| --- | --- | --- | --- | --- | --- | --- | --- |
| FCR-2601 | 2026-06-16 | PF-317A | FPF-1600-GF | B-1600-2606 | FKM bowl seal | COMPLETE | Label verified against field survey NFS-015 |
| FCR-2602 | 2026-06-16 | AF-317A | AFE-1600-MC | B-MC-2606 | FKM bowl seal | COMPLETE | Label verified against field survey NFS-016 |
| FCR-2603 | 2026-06-16 | CA-D-317A | GSK-FKM-317 | GSK-2606-04 | FKM tower gasket | COMPLETE | One set installed; second set stored |
| WO-317-06 | 2026-06-17 | CA-C-317A | OSE-1600-LS | OSE-2606-11 | Low-carryover media | COMPLETE | Installed oil separator element; service label NFS-029 |

# 3. Removed and superseded elements

| Component | Removed/legacy part | Historic date | Evidence | Disposition |
| --- | --- | --- | --- | --- |
| PF-317A | FPF-1400-GF | 2023-08-04 | Legacy element; shorter end-cap geometry | Not suitable for current FPF-1600 housing |
| AF-317A | AFE-1400-MC | 2023-08-04 | Legacy element from DH-1400 package | Not suitable for current AFE-1600 bowl |
| CA-C-317A | OSE-1500-ST | 2019-09-22 | Standard carryover element for VX-1500 | Superseded by current VX-1600E low-carryover element |

# 4. Desiccant and purge retrofit history

| Record | Date | Work scope | Installed item | Configuration | Status | Note |
| --- | --- | --- | --- | --- | --- | --- |
| FCR-2408 | 2024-09-18 | Desiccant charge | 486 kg DA-ALMS-7030 | Activated alumina / molecular sieve 70/30 | COMPLETE | Load-cell ticket and hatch label agree |
| FCR-2409 | 2024-09-18 | Purge valve kit | PVK-HPR-24 | Heated purge; OR-317-24 | COMPLETE | Controller setting commissioned at 8.0 percent |
| FCR-2410 | 2024-09-19 | Legacy plate retention | DH-1400 plate retained | Historical plate only | NOTED | Plate retained for vessel traceability; not current model authority |

# 5. Post-change differential-pressure observations

| Timestamp | Component | Stable DP psig | Local limit psig | Line-level interpretation | Record status |
| --- | --- | --- | --- | --- | --- |
| 2026-06-22 09:00 | PF-317A | 1.21 | 1.50 | Below local stable limit | PASS |
| 2026-06-22 09:15 | CA-D-317A dryer | 3.75 | 4.00 | Below local stable limit | PASS |
| 2026-06-22 09:30 | AF-317A | 1.10 | 1.00 | Above local stable limit | REVIEW |
| 2026-06-22 10:15 | AF-317A | 1.16 | 1.00 | Above local stable limit despite panel PASS label | REVIEW |

# 6. Commercial descriptions requiring corroboration

Quote lines Q-317-002, Q-317-004, Q-317-006, Q-317-008, Q-317-010, Q-317-012, and Q-317-015 carry commercial statuses such as ACCEPTED, but they do not match the installed configuration. Installed field labels, completed closeout records, delivery batches, and current equipment model evidence take precedence.

# 7. Evidence gaps and retained limitations

The original manufacturer batch certificate for prefilter batch B-1600-2606 was not included in the package. Installed identity is nevertheless supported by the end-cap label, delivery record DEL-2601, and closeout FCR-2601. The gap affects manufacturer batch traceability only and does not prevent identification of the installed element.

No full dryer vessel desiccant removal record was provided after the 2024 charge. The 486 kg fill ticket, hatch label, purge retrofit record, and current field survey consistently identify the 70/30 activated alumina and molecular sieve charge.